## Table 1
BACKGROUND | Glassboro Public Schools Lead in Drinking Water Action Plan
On July 13, 2016 the State Board of Education adopted regulations regarding testing for lead in drinking water in public schools. The regulations require testing in all drinking water outlets within 365 days of the effective date of the regulations. All districts were to develop a lead sampling plan to govern the collection and analysis of drinking water samples. Samples were to be sent to a certified testing laboratory for analysis. The results of these tests must be available at the school facility and on the district website. In addition, NJDOE is to be notified of all outlets that exceed the exceeds the maximum permissible lead level. And the measures to be taken to ensure that adequate drinking water has been made available to all students and staff. TESTING On May 3rd, 2022 the Board authorized a contract with the district’s environmental consultant, Environmental Design, Inc. to provide services related to lead testing in drinking water outlets. The original sampling plan was developed in June of 2017 and the following samples were collected at all identified outlets using the same plan. Samples were sent to EMSL Analytical, Inc. for analysis. Outlets exceeding the maximum permissible lead level of 15 parts per billion and remedial actions taken are detailed in the chart below:
School | Location/Description | OutletCode | Lead Level (ppb) | Remedial Action
Beach Administration Building | Water Fountain in hall | WF001 | 47.1 | Removed
Beach Administration Building | Sink in Mechanical (Room 9) | S004 | 24.7 | Removed.
Beach Administration Building | Ice Machine in Mechanical (Room 9) | IM005 | 26.2 | Turned Off
Dorothy L. Bullock Elementary School | Sink A-4 | S002 | 42.8 | "Hand Washing Only" sign posted
Dorothy L. Bullock Elementary School | Sink A-14 | S013 | 7.87 | “Hand Washing Only “ sign posted. Will leave as hand wash only.
Dorothy L. Bullock Elementary School | Bubbler A-14 | B013 | 31.7 | “Hand Washing Only “ sign posted Turned off
Dorothy L. Bullock Elementary School | Sink Kitchen | S026 | 1.91 | Fixture replaced. Second sample below max lead level
Dorothy L. Bullock Elementary School | Sink C-41 | S066 | 65.8 | “Hand Washing Only “ sign posted Leaving as hand was only sink
Dorothy L. Bullock Elementary School | Sink C-40 | SO67 | 50.2 | “Hand Washing Only “ sign posted Leaving as hand wash only sink
Dorothy L. Bullock Elementary School | Sink Kitchen Dishwash (L) by Freezer | S023 | 316 | "HAND WAS ONLY" SIGN POSTED Will replace faucet and retest
Dorothy L. Bullock Elementary School | Sink 2-36 | S033 | 26.8 | "HAND WAS ONLY' SIGN POSTED
Dorothy L. Bullock Elementary School | Sink C-30 | WF007 | 52.1 | "HAND WAS ONLY" SIGN POSTED
Dorothy L. Bullock Elementary School | Sink C-33 | S047 | 93.1 | "HAND WAS ONLY" SIGN POSTED
Glassboro High School | Sink Conference room | S002 | 23.8 | "HAND WAS ONLY" SIGN POSTED
Glassboro High School | Sink E106 | S003 | 1.02 | “Hand Washing Only “ sign posted Leave as posted
Glassboro High School | Bathroom Sink Nurse | S004 | 10.6 | “Hand Washing Only “ sign posted Leave as posted
Glassboro High School | Sink A131 (exterior wall) | S008 | 6.26 | “Hand Washing Only “ sign posted Leave as posted
Glassboro High School | Sink A141 | S009 | 93.8 | “Hand Washing Only “ sign posted
Glassboro High School | Sink A138 | S016 | 1.68 | “Hand Washing Only “ sign posted Leave as posted
Glassboro High School | WF across from A137 | WF004 | 879 | Turned Off
Glassboro High School | Sink in Backstage Dressing Room (E102B) | S025 | 58.6 | “Hand Washing Only “ sign posted
Glassboro High School | WF across from B103 | WF007 | <1.OO | NEW FILTERED WATER FOUNTAIN
Glassboro High School | Sink B112C | S028 | 4.51 | “Hand Washing Only “ sign posted Leave as posted
Glassboro High School | Sink Kitchen | S041 | 1.36 | FIXTURE CHANGED RESULTS acceptable
Glassboro High School | Sink Kitchen | S042 | 1.34 | Fixture changed, outlet retested Results within acceptable limits
Glassboro High School | Sink C107 | S055 | 15.7 | “Hand Washing Only “ sign posted
Glassboro High School | Hose Bib - outside A102 | HB002 | 92.6 | “Hand Washing Only “ sign posted
Glassboro High School | Hose Bib- outside A145 | HB004 | 47.8 | “Hand Washing Only “ sign posted
Glassboro High School | Hose Bib - outside A144 | HB005 | 539 | “Hand Washing Only “ sign posted
Glassboro High School | Hose Bib - outside B116 | HB007 | 26.2 | “Hand Washing Only “ sign posted
Glassboro High School | Hose Bib (Concession Stand) | HB008 | 18.3 | “Hand Washing Only “ sign posted
Glassboro High School | Sink C108 | S057 | 16.2 | “Hand Washing Only “ sign posted
Glassboro High School | Sink Vice Principal Bathroom | S059 | 99 | “Hand Washing Only “ sign posted
Glassboro High School | Sink Lady Locker Room Office | S062 | 3.39 | “Hand Washing Only “ sign posted
Glassboro Intermediate School | Sink SRO Office Room 215 | S022 | 15.6 | "Hand Washing Only" sign posted
Glassboro Intermediate School | WF in Hall outside 213 | WF004 | 66.8 | Turned Off
Glassboro Intermediate School | Boys restroom sink; by Room 202 | S031 | ND | “Hand Washing Only “ sign posted Leave as posted
Glassboro Intermediate School | Sink 305 | S034 | 2.23 | “Hand Washing Only “ sign posted Leave as posted
Glassboro Intermediate School | Sink in PAC1 (ANNEX) | S035 | 6.78 | “Hand Washing Only “ sign posted Leave as posted
Glassboro Intermediate School | Sink in PAC1 (ANNEX) | S036 | 9.38 | “Hand Washing Only “ sign posted Leave as posted
Glassboro Intermediate School | Sink Girl's restroom (ANNEX) | S038 | 1.07 | “Hand Washing Only “ sign posted Leave as posted
J. Harvey Rodgers Elementary School | Bubbler B-3 | B002 | 161 | Turned off
J. Harvey Rodgers Elementary School | Bubbler B-2 | B003 | 228 | Turned Off
J. Harvey Rodgers Elementary School | Sink B-3A bathroom | S009 | 2.89 | “Hand Washing Only “ sign posted Leave as posted
J. Harvey Rodgers Elementary School | Sink B-3B bathroom | S010 | 2.52 | “Hand Washing Only “ sign posted Leave as posted
J. Harvey Rodgers Elementary School | Sink B-2A Bathroom | S012 | 1.12 | “Hand Washing Only “ sign posted Leave as posted
J. Harvey Rodgers Elementary School | Sink B-2 | S014 | 745 | “Hand Washing Only “ sign posted
J. Harvey Rodgers Elementary School | Sink B-5 | S017 | 0 | “Hand Washing Only “ sign posted Leave as posted
J. Harvey Rodgers Elementary School | Bubbler B-5 | B004 | 80.3 | Fixture Removed
J. Harvey Rodgers Elementary School | Bubbler B-8 | B005 | 19.3 | Fiixture removed
J. Harvey Rodgers Elementary School | Sink A-8 | S029 | 7.93 | “Hand Washing Only “ sign posted Leave as posted
J. Harvey Rodgers Elementary School | WF outside room B-7 | WF005 | 568 | Turned off
J. Harvey Rodgers Elementary School | Sink in 241 Faculty Room | S037 | 38.2 | "Hand Washing only" Sign posted
J. Harvey Rodgers Elementary School | Hose Bib- outside Kitchen Area | HB002 | 1730 | “Hand Washing Only “ sign posted
J. Harvey Rodgers Elementary School | Hose Bib in courtyard | HB003 | 79.2 | “Hand Washing Only “ sign posted
J. Harvey Rodgers Elementary School | Hose Bib- outside A-8 | HB004 | 38.6 | “Hand Washing Only “ sign posted
Thomas E. Bowe Elementary School | Sink D144 | S003 | 145 | "Hand Washing Only" sign posted
Thomas E. Bowe Elementary School | Bubbler in Media Office | B001 | 459 | Fixture Removed
Thomas E. Bowe Elementary School | Sink D103 | S005 | 5.8 | “Hand Washing Only “ sign posted Leave as posted
Thomas E. Bowe Elementary School | WF in Hall by C132 | WF004 | ND | Outlet retested, results now within acceptable Limits.
Test results have been posted on the district website and are available at each school. Parents have received a letter detailing the outlets that exceeded the maximum permissible lead level and the corrective actions taken. The NJDOE has also been notified.
The fact that excessive lead levels were not detected at every outlet would seem to point to individual fixtures or fittings as the source of the contamination.